## Sheet1
| Voltage |  | Unit
Power Consumed by the node | Volts | Current | Power | QTY | Net
| (PSU efficiency) | Amps | Watts |  | Watts | Notes
Front End Modules (FEM) | 5 | 0.195 | 0.975 | 12 | 11.7 | The FEM heat is NOT dissipated inside the Node Enclosure
Post Amplificer Modules (PAM) : External to Node Enclosure | 5 | 0.4725 | 2.3625 | 12 | 28.35
FEM linear/analog power generation and distribution | 0.45 |  | 14.3 | 1 | 14.3 | linear power supplies are about 45% efficient
PAM linear/analog power generation and distribution | 0.45 |  | 34.65 | 1 | 34.65 | linear power supplies are about 45% efficient
SNAPv2 | 12 | 2 | 24 | 4 | 96 | 1.6Amp is a measured values; use 2A for margin
White Rabbit | 5 | 1.6 | 8 | 1 | 8
Beaglebone | 5 | 2 | 10 | 1 | 10
+12V switching/digital power generation and distribution | 0.8 |  | 24 | 1 | 24 | switching power supplies are about 80% efficient
+5V switching/digital power generation and distribution | 0.8 |  | 4.5 | 1 | 4.5 | switching power supplies are about 80% efficient
Interface Logic and Monitoring | 5 | 1 | 5 | 1 | 5
Externally mounted centrifugal fan | 230 | 0.32 | 66 | 1 | 66 | The Fan heat is NOT dissipated inside the Node Enclosure. Operating point on curve is 0.32A 66W. The fan is rate for 0.36A and 90W.
Total |  |  |  |  | 302.5
Power dissipated inside the Node Enclosure |  |  |  |  | 224.8
Power dissipated at the feeds |  |  |  |  | 11.7
Power dissipated at the centrifugal fan |  |  |  |  | 66 | This heat will be handled by long run of buried ducting between the centrifugal fan and the Node Enclosure
input VAC voltage | 230
Input VAC currents (nominal operating mode) | power factor | VAC input Amps
FEM linear/analog power generation and distribution | 0.65 | 0.17391 |  |  |  | generic value from generic linea power supply : http://www.acopian.com/linear-power-supply-vs-switching-power-supply-vs-unregulated-power-supply.html
PAM linear/analog power generation and distribution | 0.65 | 0.4214 |  |  |  | generic value from generic linea power supply : http://www.acopian.com/linear-power-supply-vs-switching-power-supply-vs-unregulated-power-supply.html
+12V switching/digital power generation and distribution | 0.93 | 0.56101
+5V switching/digital power generation and distribution | 0.93 | 0.12856
Externally mounted centrifugal fan | 0.89674 | 0.32 |  |  |  | (assuming fan is at operating point 2 (see datasheet)
VAC current input to the Node Enclosure |  | 1.6049 |  |  |  | includes current for FEM and external centrifugal fan
Inrush Input VAC currents
When the Node Enlcosure is "turned on" only the +5V supply turns on.
Then if the internal computer decides everything is ok then it will turn on the other VAC consumers and it can do this 1consumer at a time.
FEM linear/analog power generation and distribution | 40 |  |  |  |  | total guess for the TBD Lineare power supply inrush
PAM linear/analog power generation and distribution | 40 |  |  |  |  | total guess for the TBD Lineare power supply inrush
+12V switching/digital power generation and distribution | 50
+5V switching/digital power generation and distribution | 35
Externally mounted centrifugal fan
Air Flow | 106 | CFM
Air Flow | 3.0016 | Cubic meters per minute
Pipe Diameter | 110 | mm
Pipe Wall thickness | 3 | mm
Pipe Area Interior | 8494.8665 | mm squared
Pipe Area Exterior | 9503.3178 | mm squared
Air Speed | 353.3411 | meters per minute
| 5.889 | meters per second
| 17.8196 | ft per second
http://www.engineeringtoolbox.com/convective-heat-transfer-d_430.html
heat transfer coeff | 30 | Watts / (meter squared * Kelvin)
SNAP back cover surface area | 80 | inches squared | ignoring heat path to top cover
| 0.051613 | meters squared
Max FPGA junction temperature | 80 | Celsius
Thermal Resistance from junction to case | 0.2 | Celsius/Watt
Thermal Resistance from case to PCB | 0.1 | Celsius/Watt
Thermal Resistance of the Gap Pad 3.0 bottom | 1.5 | Celsius/Watt
Thermal Resistance of the bottom heat sink | 0.0495 | Celsius/Watt
Thermal Resistance of Heat sink to the bottom cover | 0.02 | Celsius/Watt
Thermal Resistance from junction to bottom cover | 1.8695 | Celsius/Watt
FPGA power as function of SNAP power | 0.8
Maximum allowed bottom cover temperature | 44.1056 | Celsius
Maximum node air temperature | 28.6056 | Celsius
Air Temperature of node inlet year round | 21 | Celsius
Air Temperature margin | 4 | Celsius
Rise in air temperature dut to PAM | 3 | Celsius
Maximum node air temperatu