## Sheet1
Solar heat gain is not, at all, accounted for in this spreadsheet. Even without it the numbers are depressing enough

	Voltage		Unit
Power Consumed by the node	Volts	Current	Power	QTY	Net
	(PSU efficiency)	Amps	Watts		Watts		Units	Notes
Front End Modules (FEM) : External to the Node Enclosure	5	0.195	0.975	12	11.7			The FEM heat is NOT dissipated inside the Node Enclosure
Post Amplificer Modules (PAM)	5	0.4725	2.3625	12	28.35
FEM linear/analog power generation and distribution	0.5		11.7	1	11.7			linear power supplies are about 45% efficient
PAM linear/analog power generation and distribution	0.5		28.35	1	28.35			linear power supplies are about 45% efficient
PAM margin	5	1	5	1	5
SNAPv2	12	1.85	22.2	4	88.8			1.85Amp is a measured value with almost final gateware and prototype I2C Mezzanine card installed. For margin could use 2A (max)
White Rabbit	5	1.6	8	1	8
Arduino Ethernet (was Beaglebone and before that was Raspberry Pi)	5	0.2	1	1	1			Arduino Ethernet is very low power relative to the Beaglebone Black and Raspberry Pi
+12V switching/digital power generation and distribution	0.8		22	1	22.2			switching power supplies are about 80% efficient
+5V switching/digital power generation and distribution	0.8		2.3	1.00	2.25			switching power supplies are about 80% efficient
Interface Logic and Monitoring	5	1	5	1	5
Externally mounted LARGER centrifugal fan : actually purchased	230	1.2	179	1	179			The Fan heat is NOT dissipated inside the Node Enclosure. Operating point on curve is from PA(static)=270Pa. CFM=0.06M**3/sec, P(W)=180W.CBB-60N
Externally mounted LARGER centrifugal fan : Not actually purchased ?	230	2.2	500	0	0			The Fan heat is NOT dissipated inside the Node Enclosure. Operating point on curve is from PA(static)=270Pa. CFM=950m**3/H, P(W)=500. Systemair EX 140-2C This particular fan is probably not ideal fit for the underground pipes, RFI vents, and Node Enclosure
Externally mounted SMALLER centrifugal fan	230	0.32	66	0	0			The Fan heat is NOT dissipated inside the Node Enclosure. Operating point on curve is 0.32A 66W. The fan is rate for 0.36A and 90W. Ziehl-abegg S-series RG12S-2E http://www.farnell.com/datasheets/2032679.pdf

Total					391.35

Power dissipated inside the Node Enclosure					379.65
Power dissipated at the feeds					11.7
Power dissipated at the centrifugal fan					0			This heat will be handled by long run of buried ducting between the centrifugal fan and the Node Enclosure

input VAC voltage	230

Input VAC currents (nominal operating mode)	power factor	VAC input Amps
FEM linear/analog power generation and distribution	0.65	0.157					generic value from generic linear power supply : http://www.acopian.com/linear-power-supply-vs-switching-power-supply-vs-unregulated-power-supply.html
PAM linear/analog power generation and distribution	0.65	0.413					generic value from generic linear power supply : http://www.acopian.com/linear-power-supply-vs-switching-power-supply-vs-unregulated-power-supply.html
+12V switching/digital power generation and distribution	0.93	0.519
+5V switching/digital power generation and distribution	0.93	0.076
Externally mounted centrifugal fan	0.90	0.000					(assuming fan is at operating point 2 (see datasheet)

VAC current input to the Node Enclosure		1.164
VAC current input to the Node (Total)		1.164					Includes current for external centrifugal fan

Inrush Input VAC currents
When the Node Enlcosure is "turned on" only the +5V supply turns on.
Then if the internal computer decides everything is ok then it will turn on the other VAC consumers and it can do this 1consumer at a time.
FEM linear/analog power generation and distribution	40					total guess for the TBD Lineare power supply inrush
PAM linear/analog power generation and distribution	40					total guess for the TBD Lineare power supply inrush
+12V switching/digital power generation and distribution	50
+5V switching/digital power generation and distribution	35
Externally mounted centrifugal fan

	Smaller fan??? Ziehl-abegg S-series RG12S-2E	Larger Fan actually purchased CBB-60N	Larger Fan NOT purchased System Air EX 140-2C	Systemair CE 140 S-125. Was considered then dropped due to indoor unit. 67L/sec 1 liter is 0.1m*0.1m*0.1m	NO FAN	NO FAN
Air Flow : as in the datasheet operating point 2. At or around 270 Pa due to the many meters of pipe. See calculations elsewhere. And datasheet	180	216	950	241.2				Cubic meters per hour
Air Flow	105.94	127.13	559.15	141.96				CFM
Air Flow	3.000	3.600	15.833	4.020				Cubic meters per minute
Pipe Diameter	110	110	110	110				mm
Pipe Wall thickness	3	3	3	3				mm

Pipe Area Interior	8495	8495	8495	8495				mm squared
Pipe Area Exterior	9503	9503	9503	9503				mm squared
Air Speed through the interior of the pipe	353.2	423.8	1863.9	473.2				meters per minute
	5.9	7.1	31.1	7.9				meters per second
	17.8	21.4	94.0	23.9				ft per second	Freedom units

The air in the pipe must be dispersed across the width of the rack so as to cool all the different modules installed.
width of rack	431.8	431.8	431.8	431.8	431.8	431.8		mm	Could slightly improve things if, for example, disperse the air across only 12 of the 17” width of the rack are used for the 12 PAMs and 4 SNAPv2s
depth of components to be cooled	254	254	254	254	254	254		mm	say just first 10” of depth of the rack are to be cooled. The SNAPv2s extend back only 8”
Area for the air to flow in the Rack	109677.2	109677.2	109677.2	109677.2	109677.2	109677.2		mm squared
	0.46	0.55	2.41	0.61	0.00	0.00		meters per second	assume perfect dispersion baffles of some sort

http://www.engineeringtoolbox.com/convective-heat-transfer-d_430.html	Watts / (meter squared * Kelvin)					Equation and curve good for velocities 2 to 20m/sec

2017nov30: SNAPv2s shut down when running EMC tests at the VLA sitting on the bench w/ no forced airflow. Once 5” box fan (120VAC) blowing at them they kept running. The EMC chamber temp was unknown; guess about 25degC at the high side
2017nov30: They ran for quite a while without airflow. Not sure how long – hour or two ?
2017dec18: SNAPv2 sitting in open air on the bench measure U37 near the PWM controllers the hottest at about 107degF. Other DC-Dcs about 5 to 10degF cooler.

http://www.sfu.ca/~mbahrami/ENSC%20388/Notes/Natural%20Convection.pdf
max temp of the bottom cover					65.0	65.0	Celsius
					149.0	149.0	degF	Freedom units
estimated (still) air temperature					20	20
					68.0	68.0	degF	Freedom units
Tfilm					42.5	42.5
					108.5	108.5	degF	Freedom units
					315.5	315.5	Kelvin
Beta					3.17E-03	3.17E-03
K					2.69E-02	2.69E-02	W/mK
V					1.65E-05	1.65E-05
Pr					0.7	0.7
chassis height					0.3	0.3	m
chassis depth					0.2	0.2	m
Rayleigh number					5.89E+07	5.89E+07
Nu					3.89E+01	3.89E+01
heat transfer coeff					4.11E+00	4.11E+00	W/(K*M**2)

heat transfer coeff : what is value to use ???	14	14	16.0	16	4.1	4.1	W/(K*M**2)	For smaller fan(s): use lower limit from the curve found online then further scale that down because airflow is below the lower limit of the curve (~~0.5 vs 2 m/sec)

SNAP back cover surface area	80	80	80	80	80	80	inches squared
	0.1032256	0.1032256	0.1032256	0.1032256	0.1032256	0.1032256	meters squared; * 2 for the top and bottom covers

	Smaller fan	Smaller fan	Larger fan	Larger fan	NO FAN	NO FAN
	FPGA	any of the DC-DC converters	FPGA	any of the DC-DC converters	FPGA	any of the DC-DC converters
		hanging off of U42: eg U37		hanging off of U42: eg U37		hanging off of U42: eg U37
Max IC junction temperature	85.0	80.0	85.0	80.0	85.0	80.0	Celsius
	185.0	176.0	185.0	176.0	185.0	176.0	degF	Freedom units
Thermal Resistance from junction to case	0.2	5.0	0.2	5.0	0.2	5.0	Celsius/Watt	TI DC-DC: guess low-ish value from http://cds.linear.com/docs/en/packaging/Thermal_table_Aug_2017.pdf
Thermal Resistance from case to PCB	0.1	5.0	0.1	5.0	0.1	5.0	Celsius/Watt	TI DC-DC: guess the 3 center vias have, each, about 25degC/W resistance or net of about 8.3; other pins are parallel heat paths so guess 5degC/W?
Thermal Resistance of the Gap Pad 3.0 bottom	1.5	0.0	1.5	0.0	1.5	0.0	Celsius/Watt	TI DC-DC: to go across the copper planes. Guess low value – the planes are pretty good conductors of heat
Thermal Resistance of the bottom heat sink	0.0	0.1	0.0	0.1	0.0	0.1	Celsius/Watt	TI DC-DC : guess low value for board to frame
Thermal Resistance of Heat sink to the bottom cover	0.0		0.0	0.0	0.0	0.0	Celsius/Watt

Thermal Resistance from junction to bottom cover	1.9	10.1	1.9	10.1	1.9	10.1	Celsius/Watt	FPGA: Ignore the heat path to the top panel

IC power	8.0	1.0	8.0	1.0	8.0	1.0	Watts	See the Xilinx prediction spreadsheet 7_Series_XPE_2017_3_HERA.xlsm
Maximum allowed bottom cover temperature	70.0	69.9	70.0	69.9	70.0	69.9	Celsius
Maximum node air temperature at the SNAPv2s	54.7	54.5	56.6	56.4	17.8	17.6	Celsius
	130.4	130.1	133.9	133.6	64.0	63.7	degF	Freedom units

Heat dissipated by the PAM and FEM hardware located below the SNAPv2s	73.4	73.4	73.4	73.4	73.4	73.4	Watts	see numbers at the top of this spreadsheet
surface area of the PAM and FEM hardware	0.11	0.11	0.11	0.11	0.11	0.11	Meters**2
heat transfer coeff	14	14	16.0	16.0	4.1	4.1	W/(K*M**2)
rise in air temperature due to PAM and FEM hardware	47.80	47.80	41.83	41.83	162.72	162.72	Celsius
	118.0					degF	Freedom units

	Smaller fan	Smaller fan	Larger fan	Larger fan	NO FAN	NO FAN
Maximum node air temperature at the bottom side of the PAM and FEM components assuming the air for the SNAPv2s comes only from the PAM and FEM components	6.88	6.72	14.78	14.61	-144.97	-145.13	Celsius
	44.4	44.1	58.6	58.3	-228.9	-229.2	degF	Freedom units

Baffles, and fans if necessary, could be installed above the PAM and FEM so the air that passes over those components and thus warms up is directed to the back of the Node Enclosure – and is Not used to “cool” the SNAPv2s.
This is the airflow as used in the F and X Racks in the HERA container. All airflow within each module is cold air in from the front and warm air exhausts out the back.