## Sheet1
	Voltage		Unit
Power Consumed by the node	Volts	Current	Power	QTY	Net
	(PSU efficiency)	Amps	Watts		Watts	Notes
Front End Modules (FEM)	5	0.195	0.975	12	11.7	The FEM heat is NOT dissipated inside the Node Enclosure
Post Amplificer Modules (PAM) : External to Node Enclosure	5	0.4725	2.3625	12	28.35
FEM linear/analog power generation and distribution	0.45		14.3	1	14.3	linear power supplies are about 45% efficient
PAM linear/analog power generation and distribution	0.45		34.65	1	34.65	linear power supplies are about 45% efficient
PAM margin	5	2	10	1	10
SNAPv2	12	1.85	22.2	4	88.8	1.6Amp is a measured values; use 2A for margin
White Rabbit	5	1.6	8	1	8
Arduino Ethernet (was Beaglebone and before that was Raspberry Pi)	5	0.2	1	1	1	Arduino Ethernet is very low power relative to the Beaglebone Black and Raspberry Pi
+12V switching/digital power generation and distribution	0.8		22	1	22.2	switching power supplies are about 80% efficient
+5V switching/digital power generation and distribution	0.8		2.3	1.00	2.25	switching power supplies are about 80% efficient
Interface Logic and Monitoring	5	1	5	1	5
Externally mounted centrifugal fan	230	0.32	66	1	66	The Fan heat is NOT dissipated inside the Node Enclosure. Operating point on curve is 0.32A 66W. The fan is rate for 0.36A and 90W.

Total					292.25

Power dissipated inside the Node Enclosure					214.55
Power dissipated at the feeds					11.7
Power dissipated at the centrifugal fan					66	This heat will be handled by long run of buried ducting between the centrifugal fan and the Node Enclosure

input VAC voltage	230

Input VAC currents (nominal operating mode)	power factor	VAC input Amps
FEM linear/analog power generation and distribution	0.65	0.174				generic value from generic linea power supply : http://www.acopian.com/linear-power-supply-vs-switching-power-supply-vs-unregulated-power-supply.html
PAM linear/analog power generation and distribution	0.65	0.488				generic value from generic linea power supply : http://www.acopian.com/linear-power-supply-vs-switching-power-supply-vs-unregulated-power-supply.html
+12V switching/digital power generation and distribution	0.93	0.519
+5V switching/digital power generation and distribution	0.93	0.076
Externally mounted centrifugal fan	0.90	0.320				(assuming fan is at operating point 2 (see datasheet)

VAC current input to the Node Enclosure		1.257
VAC current input to the Node (Total)		1.577				Includes current for external centrifugal fan

Inrush Input VAC currents
When the Node Enlcosure is "turned on" only the +5V supply turns on.
Then if the internal computer decides everything is ok then it will turn on the other VAC consumers and it can do this 1consumer at a time.
FEM linear/analog power generation and distribution	40					total guess for the TBD Lineare power supply inrush
PAM linear/analog power generation and distribution	40					total guess for the TBD Lineare power supply inrush
+12V switching/digital power generation and distribution	50
+5V switching/digital power generation and distribution	35
Externally mounted centrifugal fan

Air Flow	106	CFM
Air Flow	3.002	Cubic meters per minute
Pipe Diameter	110	mm
Pipe Wall thickness	3	mm

Pipe Area Interior	8495	mm squared
Pipe Area Exterior	9503	mm squared
Air Speed	353.341129760739	meters per minute
	5.88901882934565	meters per second
	17.8195921972454	ft per second

http://www.engineeringtoolbox.com/convective-heat-transfer-d_430.html
heat transfer coeff	20	Watts / (meter squared * Kelvin)				30 to 35W/(K*m**2) for velocity 10 to 20m/sec. Use lower value because not all air will blow past the components to be cooled. At0 m/sec value drops down to ~10.5 W/(K*m**2)

SNAP back cover surface area	80	inches squared	ignoring heat path to top cover
	0.0516128	meters squared

2017nov30: SNAPv2s shut down when running EMC tests at the VLA sitting on the bench w/ no airflow. Once 5” box fan (120VAC) blowing at them they kept running.
2017dec18: SNAPv2 sitting in open air on the bench measure U37 near the PWM controllers the hottest at about 107degF. Other DC-Dcs about 5 to 10degF cooler.

	FPGA	any of the DC-DC converters
		hanging off of U42: eg U37
Max IC junction temperature	85	80			Celsius
Thermal Resistance from junction to case	0.2	8			Celsius/Watt	TI DC-DC: guess middle/low value from http://cds.linear.com/docs/en/packaging/Thermal_table_Aug_2017.pdf
Thermal Resistance from case to PCB	0.1	8.33333333333333			Celsius/Watt	TI DC-DC: guess the 3 center vias have, each, about 25degC/W resistance
Thermal Resistance of the Gap Pad 3.0 bottom	1.5	0.02			Celsius/Watt	TI DC-DC: to go across the copper planes. Guess low value – the planes are pretty good conductors of heat
Thermal Resistance of the bottom heat sink	0.0495	0.1			Celsius/Watt	TI DC-DC : guess low value for board to frame
Thermal Resistance of Heat sink to the bottom cover	0.02				Celsius/Watt

Thermal Resistance from junction to bottom cover	1.8695	16.4533333333333			Celsius/Watt

IC power	8	1			Watts	See the Xilinx prediction spreadsheet 7_Series_XPE_2017_3_HERA.xlsm
Maximum allowed bottom cover temperature	70.044	63.5466666666667			Celsius
Maximum node air temperature	48.537706987414	42.0403736540806			Celsius

Air Temperature of node inlet year round	21	Celsius
Air Temperature margin	4	Celsius
Rise in air temperature dut to PAM	3	Celsius

Maximum node air temperature